## pressure_drop
PIPING PRESSURE DROP CALCULATION
Pipe Characteristics
|  | Line Description: | Main Pipe
|  | Nominal Size | N/A |  | Absolute Roughness (ε) |  | 4.572e-05 | m
|  | Material and Schedule | N/A |  | Inside Diameter (d) |  | 729 | mm
[5 empty] | Inside Diameter (D) |  | 0.729 | m
Fluid Properties
|  | Fluid: |  |  | Average Pressure: |  | 55 | bar (a)
|  | Flow Rate (W): | 1574000 | kg / hr | Average Temperature: |  | 602 | C
[5 empty] | Specific Volume (V) |  | 0.071555
[5 empty] | Absolute Viscosity (μ) |  | 0.032915 | cP
Pressure Drop
|  | Fluid Velocity (Vel): |  | Vel = 353.678 W x V / d2 | 74.9544 | m/sec = | 4497.2612 | m/min
|  | Reynolds Number (Re): |  | Re = (Vel x D) / (V x μ) | 23200232.3967 | Turbulent
Friction Factor (f):
|  | Turbulent Flow: |  |  | 0.011102
|  | Laminar Flow: |  | f = 64 / Re
|  | Resistance Coefficients of Fittings, Valves, Etc. |  |  |  | Quantity (n): | L/D or K/f: | nL/D:
|  | elbow long 90 |  |  |  | 30 | 2 | 60
|  | butterfly valve |  |  |  | 25 | 1 | 25
|  | 0 |  |  |  | 0 | 0 | 0
|  | 0 |  |  |  | 0 | 0 | 0
|  | 0 |  |  |  | 0 | 0 | 0
|  | 0 |  |  |  | 0 | 0 | 0
|  | 0 |  |  |  | 0 | 0 | 0
|  | 0 |  |  |  | 0 | 0 | 0
|  | 0 |  |  |  | 0 | 0 | 0
[5 empty] | Sum of nL/D for all Fittings, Valves, Etc. |  |  | 85
|  | Equivalent Length of Fittings (L_F) |  | L_F = D x Sum (nL/D) |  |  | 61.965 | m
|  | Straight Pipe Length (L_P) |  |  |  |  | 100 | m
|  | Total Equivalent Pipe Length (L_TEL) |  | L_TEL = L_F + L_P |  |  | 161.965 | m
|  | Friction Head Loss (h_L) |  | h_L = f x (L_TEL / D) x (Vel^2 / 2g) |  |  | 706.3247 | m
|  | Friction Pressure Drop (ΔP): |  | ΔP = hL / (10197 V) |  |  | 0.96804 | bar
|  | Static Head: |  | [bar] = [m] / (10197 V) | 0 | m = | 0 | bar
|  | Miiscellaneous Equipment Pressure Drops |  |  | 0 | m = | 0 | bar
[6 empty] | m = |  | bar
|  | TOTAL PRESSURE DROP |  |  |  |  | 0.96804 | bar

## data
Name | Value
epsilon | 4.572e-05
d | 729
D | 0.729
flow_rate | 1574000
p_avg | 55
t_avg | 602
V | 0.071555
mu | 3.2915e-05
Vel_m_sec | 74.9544
Vel_m_min | 4497.2612
Re | 23200232.3967
f | 0.011102
turbulence | Turbulent
nL/D | 1
L_F | 61.965
L_P | 100
L_TEL | 161.965
h_L | 706.3247
dP | 0.96804
static_head_m | 0
static_head_bar | 0
misc_pressure_drop_m | 0
misc_pressure_drop_bar | 0
total_pressure_drop | 0.96804
line_description | Main Pipe
nominal_size | N/A
material_and_schedule | N/A

## fittings
name | quantity | K/f | nL/D
elbow long 90 | 30 | 2 | 60
butterfly valve | 25 | 1 | 25