## wall_thickness
MINIMUM WALL THICKNESS FOR PIPE UNDER INTERNAL PRESSURE
Pipe and System Characteristics
|  | Pipeline Identification | Main Pipe
|  | Applicable Pipe Sizes | N/A | Fluid | Main Steam
|  | BREI Pipe Classification | N/A | Design Pressure (P) | 60 | bar (g)
|  | ASTM Specification | N/A | Design Temperature | 610 | C
Formula for Minimum Wall Thickness
| P = | Internal Design Pressure |  |  | 60 | bar
| d = | Internal Diameter (mm) |  |  | 729 | mm
| SE = | Maximum Allowable Stress Specified in B31.1 Appendix A = |  |  | 0 | bar
| Y = | Coefficient with Value Specified in B31.1 Table 104.1.2A = |  |  | 0 | mm
| A = | Additional Thickness Allowed for Corrosion, Erosion, and/or Mechanical Strength = |  |  | 0 | mm
| MFG = | Manufacturer's Wall Thickness Tolerance = |  |  | 0
| BEND = | Multiplier for Additional Thickness for Bending Specified in B31.1 Table 102.4.5 |  |  | 0
| T_n = | Nominal Wall Thickness Required (mm) |  |  | 0 | mm
| T_m = | Minimum Wall Thickness (mm) |  |  | 0 | mm
| OD = | Outer Diameter (mm) |  |  | 0 | mm

## data
Name | Value
P | 60
T | 610
d | 729
SE | 832.61
Y | 0.7
A | 0
MFG | 0.125
BEND | 1
T_m | 26.8472
T_n | 30.6825
OD | 782.6944
pipeline_identification | Main Pipe
applicable_pipe_sizes | N/A
BREI | N/A
ASTM | N/A
fluid | Main Steam