## pressure_drop
PIPING PRESSURE DROP CALCULATION
Pipe Characteristics
Line Description:
|  | Nominal Size |  | Absolute Roughness (ε) |  |  | m
|  | Material and Schedule |  | Inside Diameter (d) |  |  | mm
|  |  |  | Inside Diameter (D) |  |  | m
Fluid Properties
|  | Fluid: |  | Average Pressure: |  |  | bar (a)
|  | Flow Rate (W): | kg / hr | Average Temperature: |  |  | C
Specific Volume (V)
|  |  |  | Absolute Viscosity (μ) |  |  | cP
Pressure Drop
|  | Fluid Velocity (Vel): | Vel = 353.678 W x V / d2 |  | m/sec = |  | m/min
|  | Reynolds Number (Re): | Re = (Vel x D) / (V x μ)
Friction Factor (f):
Turbulent Flow:
|  | Laminar Flow: | f = 64 / Re
|  | Resistance Coefficients of Fittings, Valves, Etc. |  |  | Quantity (n): | L/D or K/f: | nL/D:
Sum of nL/D for all Fittings, Valves, Etc.
|  | Equivalent Length of Fittings (L_F) | L_F = D x Sum (nL/D) |  |  |  | m
|  | Straight Pipe Length (L_P) |  |  |  |  | m
|  | Total Equivalent Pipe Length (L_TEL) | L_TEL = L_F + L_P |  |  |  | m
|  | Friction Head Loss (h_L) | h_L = f x (L_TEL / D) x (Vel^2 / 2g) |  |  |  | m
|  | Friction Pressure Drop (ΔP): | ΔP = hL / (10197 V) |  |  |  | bar
|  | Static Head: | [bar] = [m] / (10197 V) |  | m = |  | bar
|  | Miiscellaneous Equipment Pressure Drops |  |  | m = |  | bar
[5 empty] | m = |  | bar
|  | TOTAL PRESSURE DROP |  |  |  |  | bar

## wall_thickness
MINIMUM WALL THICKNESS FOR PIPE UNDER INTERNAL PRESSURE
Pipe and System Characteristics
Pipeline Identification
|  | Applicable Pipe Sizes | Fluid
|  | BREI Pipe Classification | Design Pressure (P) | bar (g)
|  | ASTM Specification | Design Temperature | C
Formula for Minimum Wall Thickness
| P = | Internal Design Pressure
| d = | Internal Diameter (mm)
| SE = | Maximum Allowable Stress Specified in B31.1 Appendix A = |  | bar
| Y = | Coefficient with Value Specified in B31.1 Table 104.1.2A = |  | mm
| A = | Additional Thickness Allowed for Corrosion, Erosion, and/or Mechanical Strength =
| MFG = | Manufacturer's Wall Thickness Tolerance =
| BEND = | Multiplier for Additional Thickness for Bending Specified in B31.1 Table 102.4.5
| T_n = | Nominal Wall Thickness Required (mm) |  | mm
| T_m = | Minimum Wall Thickness (mm) |  | mm
| OD = | Outer Diameter (mm) |  | mm

## data
Name | Value
epsilon | 4.572e-05
d | 729
D | 0.729
flow_rate | 1574000
p_avg | 54.93
t_avg | 601
V | 0.071557
mu | 3.2874e-05
Vel_m_sec | 74.957
Vel_m_min | 4497.4227
Re | 23229048.9836
f | 0.011102
turbulence | Turbulent
nL/D | 1
L_F | 61.965
L_P | 100
L_TEL | 161.965
h_L | 706.3664
dP | 0.96806
static_head_m | 0
static_head_bar | 0
misc_pressure_drop_m | 0
misc_pressure_drop_bar | 0
total_pressure_drop | 0.96806

## fittings
name | quantity | K/f | nL/D
elbow long 90 | 30 | 2 | 60
butterfly valve | 25 | 1 | 25